## Dictionary
Source | ASHRAE, ANSI/ASHRAE Standard 62.1-2019. Ventilation for acceptable indoor air quality. 2019, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Inc.: Atlanta, GA.
Table 6-1 Minimum Ventilation Rates in Breathing Zone
People Outdoor Air Rate |  | L/s-person
Area Outdoor Rate |  | L/s-m2
Occupant Density |  | People/(1000ft2 or 100m2)
People Outdoor Air Rate |  | Area Outdoor Air Rate cfm/ft2

## Mech Req.
occupancy.type | People Outdoor Air Rate L/s-person | People Outdoor Air Rate cfm/person | Area Outdoor Rate L/s-m2 | Area Outdoor Air Rate cfm/ft2 | Occupant Density | Occupant density x/100
Animal Exam room | 5 | 10 | 0.9 | 0.12 | 20 | 0.2
Animal Imaging Procedure Room | 5 | 10 | 0.9 | 0.18 | 20 | 0.2
Correctional Facility Cell | 2.5 | 5 | 0.6 | 0.12 | 25 | 0.25
Correctional Facility - Booking Waiting | 3.8 | 7.5 | 0.3 | 0.06 | 50 | 0.5
Classroom (5-8) | 5 | 10 | 0.6 | 0.12 | 25 | 0.25
Classroom 9+ | 5 | 10 | 0.6 | 0.12 | 35 | 0.35
Lecture Classroom | 3.8 | 7.5 | 0.3 | 0.06 | 65 | 0.65
Lecture Hall (fixed) | 3.8 | 7.5 | 0.3 | 0.06 | 150 | 1.5
Education Libraries | 2.5 | 5 | 0.6 | 0.12 | 10 | 0.1
Multiuse assembly | 3.8 | 7.5 | 0.3 | 0.06 | 100 | 1
Bar, Cocktail lounges | 3.8 | 7.5 | 0.9 | 0.18 | 100 | 1
Restaurant | 3.8 | 7.5 | 0.9 | 0.18 | 70 | 0.7
Cafeteria/fast food dining | 3.8 | 7.5 | 0.9 | 0.18 | 100 | 1
Hotel Bedroom/living room | 2.5 | 5 | 0.3 | 0.06 | 10 | 0.1
Hotel Lobbies | 3.8 | 7.5 | 0.3 | 0.06 | 30 | 0.3
Hotel , Resort, Dormitory Multiuse assembly | 2.5 | 5 | 0.3 | 0.06 | 120 | 1.2
Bank | 3.8 | 7.5 | 0.3 | 0.06 | 15 | 0.15
Pharmacy | 2.5 | 5 | 0.9 | 0.18 | 10 | 0.1
Office Space | 2.5 | 5 | 0.3 | 0.06 | 5 | 0.05
Office Main entry | 2.5 | 5 | 0.3 | 0.06 | 10 | 0.1
Office Reception area | 2.5 | 5 | 0.3 | 0.06 | 30 | 0.3
Outpatient General exam | 3.8 | 7.5 | 0.6 | 0.12 | 20 | 0.2
Psychiatric exam/consult room | 2.5 | 6 | 0.3 | 0.06 | 20 | 0.2
Urgent Care exam Room | 3.8 | 7.5 | 0.6 | 0.12 | 20 | 0.2
Urgent Care treatment room | 3.8 | 7.5 | 0.9 | 0.18 | 20 | 0.2
Auditorium | 2.5 | 5 | 0.3 | 0.06 | 150 | 1.5
Courtroom | 2.5 | 5 | 0.3 | 0.06 | 70 | 0.7
Legs. Chambers | 2.5 | 5 | 0.3 | 0.06 | 50 | 0.5
Libraries | 2.5 | 5 | 0.6 | 0.12 | 10 | 0.1
Lobbies | 2.5 | 5 | 0.3 | 0.06 | 150 | 1.5
Museum (children's) | 3.8 | 7.5 | 0.6 | 0.12 | 40 | 0.4
Museum / Gallery | 3.8 | 7.5 | 0.3 | 0.06 | 40 | 0.4
Places of religious worship | 2.5 | 5 | 0.3 | 0.06 | 120 | 1.2
Retail Sales | 3.8 | 7.5 | 0.6 | 0.12 | 15 | 0.15
Barbershop | 3.8 | 7.5 | 0.3 | 0.06 | 25 | 0.25
Beauty and Nail salons | 10 | 20 | 0.6 | 0.12 | 25 | 0.25
Coin operated laundry | 3.8 | 7.5 | 0.6 | 0.12 | 20 | 0.2
Mall Common area | 3.8 | 7.5 | 0.3 | 0.06 | 40 | 0.4
Pet Shop | 3.8 | 7.5 | 0.9 | 0.18 | 10 | 0.1
Supermarket | 3.8 | 7.5 | 0.3 | 0.06 | 8 | 0.08
Bowling Alley | 5 | 10 | 0.6 | 0.12 | 40 | 0.4
Dance Floor | 10 | 20 | 0.3 | 0.06 | 100 | 1
Gambling casino | 3.8 | 7.5 | 0.9 | 0.18 | 120 | 1.2
Game arcades | 3.8 | 7.5 | 0.9 | 0.18 | 20 | 0.2
Gym, Sports Arena | 10 | 20 | 0.9 | 0.18 | 7 | 0.07
Health Club Aerobics | 10 | 20 | 0.3 | 0.06 | 40 | 0.4
Health Club Weightlifting | 10 | 20 | 0.3 | 0.06 | 10 | 0.1
Residential